## Slide 1: IRRADIATION-INDUCED SWELLING OF BOR-60 SMALL ROTATION PLUG STUDS
V.S. Neustroev, D.A. Sokolovsky, S.V. Belozerov, I.Yu. Zhemkov, E.I. Makarov, Yu.V. Naboishchikov, A.I. Plotnikov, N.S. Poglyad, N.I. Shirokova
JSC «SSC RIAR», Dimitrovgrad, Russia
neustroev@niiar.ru
State Scientific Center –
Research Institute of Atomic Reactors
ХI Conference of the reactor material science (Dimitrovgrad, 27-31 May 2019)

## Slide 2: Introduction
• To know the basic laws of radiation swelling from the practical point of view is necessary to extend life-time of reactors internals, made of Fe-18Cr-10Ni-Ti steel.
• For calculations when extending the life-time of non-replaceable long-irradiated elements, it is necessary to take into account the change in irradiations conditions for many years.
Purpose of the work is to specify the basic swelling formula of Fe-18Cr-10Ni-Ti steel, and on its basis to calculate the swelling of the faces of the blanket assembly E-169 wrapper and the pins of the BOR-60 small rotation plug (SRP).

## Slide 3: An empirical dose-temperature formula mainly used to calculate swelling
where S – swelling, %,
T – irradiation temperature, °С; D – damage dose, dpa; C, n, β, Tmax – constants.
S = C · Dn exp[–β(T – Tmax)2]
S = 1.04·10–2 · D1,88 exp[–1.83 ·10–4(T – 470)2], %
The constants were calculated based on the many experimental data of irradiating Fe-18Cr-10Ni-Ti steel:
0,2-0,4 dpa/year
5-20 dpa/year
S/exp[–1.83 ·10–4(T – 470)2]
Damage dose D, dpa

## Slide 4: Models for calculating the irradiation temperature and dose in BOR-60 core using in swelling formula
T = T0(1+BZ)
Chart: 
| 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450
 | 62.0496 | 70.1481 | 76.1151 | 79.7694 | 81 | 79.7694 | 76.1151 | 70.1481 | 62.0496 | 52.0658
 | 45.5051 | 46.2323 | 47.2828 | 47.6869 | 47.6061 | 46.7172 | 44.6162 | 42.0303 | 39.0404 | 34.8384 | 30.1515 | 28.1313 | 21.3 | 18.2
100,8293839 119,0758294 150,5924171 182,9383886 206,1611374 234,3601896 255,0947867 274,1706161 299,8815166 327,2511848 345,4976303 367,0616114 395,2606635 420,971564 439,2180095 450 | 47.5644 | 48.625 | 49.6856 | 49.9508 | 49.553 | 48.3598 | 47.2992 | 45.9735 | 43.7197 | 40.6705 | 38.2841 | 35.2348 | 30.3295 | 25.4242 | 21.3144 | 19.0606
E-169 assembly
Distance from the bottom of the reactor core Z, mm
Damage dose D, dpa
IR-1 and IR-2
Dmax = 81 dpa
Dmax = 50 dpa
Dmax = 48 dpa
Chart: 
| 0 | 450
 | 320 | 402
 | 484 | 484
 | 320 | 344
ТIR-1 = 484 °С
ТE-169
Temperature Т, °C
Т0 = 320 °С
Distance from the bottom of the reactor core Z, mm

## Slide 5: Parameters of the irradiation rigs IR-1 and IR-2
а)
б)
Irradiation temperature distribution of the central tubes in IR-1 (top) and in IR-2 (bottom)
5
Studied elements were central tubes of the rigs (initial diameter – 14 mm and length – 325 mm).
Central tube
489
467
444
578
556
533
Tav = 484°С
Tav = 570°С

## Slide 6: Swelling of the IR-1 and IR-2 central tubes and specifying of the formula
Chart: Damage dose D, dpa
| 20 | 40 | 47.5
расчет 1 ТР-03 | 2.7868 | 10.2576 | 14.1695
ТР-03 | 1.5214 | 1.4357 | 1.8857 | 1.5214 | 2.7 | 1.9071 | 3.6857 | 2.9786 | 3.7071 | 3.0429 | 5.7214 | 5.6357 | 6.8571 | 7.1143 | 7.1357 | 7.7571 | 8.0786 | 9.2143 | 9.6429 | 10.4357
ТР-03 степенная | 0.8779 | 0.99115 | 1.1108 | 1.2368 | 1.3691 | 1.5078 | 1.6526 | 1.8036 | 1.9608 | 2.1242 | 2.2936 | 2.4691 | 2.6507 | 2.8383 | 3.0318 | 3.2313 | 3.4368 | 3.6482 | 3.8654 | 4.0886 | 4.3176 | 4.5524 | 4.7931 | 5.0395 | 5.2917 | 5.5497 | 5.8134 | 6.0828 | 6.3579 | 6.6387 | 6.9252 | 7.2174 | 7.5152 | 7.8186 | 8.1276 | 8.4422
ТР-05 | 0.19246 | 0.278 | 0.17107 | 0.17107 | 0.00021384 | 0.34215 | 0.12831 | 0.4063 | 0.44907 | 1.2617 | 0.83399 | 1.3472 | 1.39 | 1.7321 | 2.3095 | 1.4541 | 4.619 | 0.96229
 | 0.16257 | 0.18355 | 0.2057 | 0.22904 | 0.25355 | 0.27921 | 0.30604 | 0.33401 | 0.36312 | 0.39337 | 0.42474 | 0.45725 | 0.49087 | 0.5256 | 0.56145 | 0.5984 | 0.63644 | 0.67559 | 0.71582 | 0.75715 | 0.79955 | 0.84304 | 0.8876 | 0.93324 | 0.97994 | 1.0277 | 1.0765 | 1.1264 | 1.1774 | 1.2294 | 1.2824 | 1.3365 | 1.3917 | 1.4479
рассч теор 470 | 1.6826 | 1.8997 | 2.129 | 2.3706 | 2.6242 | 2.8899 | 3.1675 | 3.457 | 3.7583 | 4.0713 | 4.3961 | 4.7325 | 5.0805 | 5.44 | 5.811 | 6.1934 | 6.5872 | 6.9923 | 7.4088 | 7.8365 | 8.2754 | 8.7255 | 9.1867 | 9.659 | 10.1424 | 10.6369 | 11.1423 | 11.6587 | 12.186 | 12.7242 | 13.2733 | 13.8333 | 14.404 | 14.9856 | 15.5779 | 16.1809
Constant С | In original formula | For IR-1 | For IR-2
For irradiating temperature | 0.0104 | 0.0054 (Т = 484°С) | 0.0010 (Т = 570°С)
For temperature using in formula Т = 470°С |  |  | 
 |  | 0.0056 | 0.0063
6
S = 5.6·10–3 · D1.88 exp[–1.83·10–4 (T – 470)2], %

## Slide 7: Temperature operation history of E-169 assembly
During the 27-year operation each face of the E-169 assembly wrapper had a different maximum temperature due to the change of adjacent assemblies.
BOR-60 reactor cartogram: 1 – CPS rod, 2 – fuel assembly, 3 – blanket assembly, 4 – research assembly,
5 – Е-04 cell (E-169)
E-169
blanket assembly
1575
1
2
3
4
5

## Slide 8: Temperature operation history of assembly E-169. Temperature corrections
Temperature dependence of D-38 face of the assembly on operating time without corrections and with corrections
The temperature of some faces may be too high due to calculation errors of energy release and linear approximation of the temperature distribution along the core height. In this regard a correction factor 0.9 was introduced for some temperatures.
Temperature, °C
Operating time, years
Initial temperature Tmax
Corrected temperature 0.9Tmax

## Slide 9: Swelling calculation results of the E-169 assembly faces
Chart: Time, years
| 0 | 1.5333333333333334 | 3.0666666666666669 | 4.5999999999999996 | 6.1333333333333337 | 7.6666666666666696 | 8.7166666666666668 | 9.7666666666666675 | 10.816666666666666 | 11.866666666666667 | 12.916666666666668 | 13.833333333333334 | 14.75 | 15.666666666666668 | 16.583333333333336 | 17.5 | 18.7 | 19.899999999999999 | 21.1 | 22.3 | 23.5 | 23.916666666666668 | 24.333333333333332 | 24.75 | 25.166666666666664 | 25.583333333333332 | 25.866666666666667 | 26.15 | 26.433333333333334 | 26.716666666666665 | 27
Д-38 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.12297 | 0.19477 | 0.31542 | 0.5086 | 0.80438 | 0.97905 | 1.076 | 1.217 | 1.4172 | 1.6948 | 2.2604 | 3.1159 | 4.7792 | 7.4827 | 11.0909 | 12.0234 | 13.299 | 15.5812 | 18.9328 | 23.3228 | 23.8916 | 24.1217 | 24.4267 | 24.8235 | 25.3301
K-1 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.10959 | 0.15066 | 0.21089 | 0.29704 | 0.41736 | 0.58188 | 0.65959 | 0.7676 | 0.9151 | 1.1153 | 1.4144 | 1.5662 | 1.7814 | 2.0804 | 2.4876 | 2.9488 | 3.1095 | 3.3165 | 3.5801 | 3.9127 | 4.4427 | 4.6111 | 4.8237 | 5.0889 | 5.4137
K-2 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.10959 | 0.15066 | 0.21089 | 0.29704 | 0.41794 | 0.58082 | 0.65554 | 0.75858 | 0.89832 | 1.0848 | 1.3839 | 1.5357 | 1.7509 | 2.0499 | 2.457 | 2.9372 | 3.1286 | 3.3825 | 3.7135 | 4.1342 | 4.6589 | 4.8192 | 5.02 | 5.2691 | 5.5745
E-03 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.11383 | 0.164 | 0.24128 | 0.35664 | 0.52445 | 0.69739 | 0.79099 | 0.92611 | 1.1168 | 1.3798 | 1.7549 | 2.0689 | 2.5859 | 3.3924 | 4.5837 | 5.2093 | 5.6839 | 6.423 | 7.507 | 8.9873 | 9.5174 | 9.6857 | 9.8983 | 10.1635 | 10.4906
Д-40 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.11168 | 0.15717 | 0.22557 | 0.32558 | 0.4686 | 0.6936 | 0.90407 | 1.2632 | 1.8365 | 2.6921 | 3.289 | 4.2467 | 6.1284 | 9.1432 | 12.9848 | 13.7062 | 14.4053 | 15.5675 | 17.3206 | 19.6843 | 20.4703 | 21.132 | 22.1843 | 23.7319 | 25.8286
Е-08 | 0 | 0.001998 | 0.0073543 | 0.015761 | 0.027069 | 0.041178 | 0.11168 | 0.15717 | 0.22557 | 0.32558 | 0.4686 | 0.65032 | 0.76145 | 0.9277 | 1.1693 | 1.5105 | 1.8892 | 2.2119 | 2.7461 | 3.5825 | 4.8199 | 5.3147 | 5.5309 | 5.8236 | 6.2119 | 6.712 | 7.2924 | 7.5418 | 7.8769 | 8.3176 | 8.885
Chart: Time, years
| 0 | 1.5333333333333334 | 3.0666666666666669 | 4.5999999999999996 | 6.1333333333333337 | 7.6666666666666696 | 8.7166666666666668 | 9.7666666666666675 | 10.816666666666666 | 11.866666666666667 | 12.916666666666668 | 13.833333333333334 | 14.75 | 15.666666666666668 | 16.583333333333336 | 17.5 | 18.7 | 19.899999999999999 | 21.1 | 22.3 | 23.5 | 23.916666666666668 | 24.333333333333332 | 24.75 | 25.166666666666664 | 25.583333333333332 | 25.866666666666667 | 26.15 | 26.433333333333334 | 26.716666666666665 | 27
К-1 | 0 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.059295 | 0.081515 | 0.1141 | 0.16072 | 0.22582 | 0.31483 | 0.35688 | 0.41532 | 0.49513 | 0.60344 | 0.76531 | 0.84743 | 0.96387 | 1.1256 | 1.3459 | 1.5955 | 1.6824 | 1.7945 | 1.9371 | 2.117 | 2.4038 | 2.4949 | 2.6099 | 2.7534 | 2.9291
К-2 | 0 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.059295 | 0.081515 | 0.1141 | 0.16072 | 0.22613 | 0.31426 | 0.35469 | 0.41044 | 0.48605 | 0.58693 | 0.74879 | 0.83092 | 0.94736 | 1.1091 | 1.3294 | 1.5892 | 1.6928 | 1.8301 | 2.0093 | 2.2369 | 2.5207 | 2.6075 | 2.7162 | 2.8509 | 3.0161
Е-03 | 0 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.061587 | 0.088734 | 0.13055 | 0.19296 | 0.28376 | 0.37733 | 0.42798 | 0.50109 | 0.60424 | 0.74656 | 0.9495 | 1.1194 | 1.3991 | 1.8355 | 2.4801 | 2.8186 | 3.0753 | 3.4752 | 4.0618 | 4.8627 | 5.1495 | 5.2406 | 5.3556 | 5.4991 | 5.6761
Д-38 | 0 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.066534 | 0.10539 | 0.17066 | 0.27518 | 0.43522 | 0.52973 | 0.58219 | 0.65849 | 0.76681 | 0.917 | 1.1197 | 1.2892 | 1.568 | 2.0027 | 2.6448 | 2.9785 | 3.2247 | 3.6052 | 4.161 | 4.9256 | 5.2334 | 5.3579 | 5.5229 | 5.7376 | 6.0117
Д-40 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.060426 | 0.085038 | 0.12205 | 0.17616 | 0.25354 | 0.37528 | 0.48916 | 0.68345 | 0.99366 | 1.4566 | 1.6702 | 1.8659 | 2.1974 | 2.7237 | 3.5064 | 3.767 | 3.8718 | 4.0112 | 4.1933 | 4.4269 | 4.7107 | 4.7975 | 4.9061 | 5.0409 | 5.2061
Е-08 | 0 | 0.0010811 | 0.0039791 | 0.0085279 | 0.014646 | 0.02228 | 0.060426 | 0.085038 | 0.12205 | 0.17616 | 0.25354 | 0.35187 | 0.41199 | 0.50194 | 0.63266 | 0.81728 | 1.0222 | 1.1968 | 1.4858 | 1.9384 | 2.6079 | 2.8756 | 2.9925 | 3.1509 | 3.361 | 3.6316 | 3.9457 | 4.0806 | 4.2619 | 4.5003 | 4.8074
C = 0,01035; initial Тmax
C = 0,0056; corrected Тmax
Method of calculating swelling by the formula | Swelling level of the faces in the top of the reactor core, % |  |  |  |  | 
 | K-1 | K-2 | Е-03 | D-38 | D-40 | Е-08
C = 0.01035; initial Тmax | 5.4 | 5.6 | 10.5 | 24.8 | 25.8 | 8.9
C = 0.0056; 0.9Тmax for D-38 and D-40 faces in a period of 17.5-25.6 years | 2.9 | 3.0 | 5.7 | 6.0 | 5.2 | 4.8
Density changes measurements | 4.6-6.5 % |  |  |  |  | 
Face
Face

## Slide 10: Sh1 pin irradiation conditions
Small rotation plug (SRP) of BOR-60 reactor
Pins and nuts of SRP
Sh1
According to the calculation of “GIROPRESS” (2009), swelling ≈ 2% and the corresponding total damage Dε = 1 were achieved by the end of 2009.
Sh1 pin irradiation conditions | Damage dose (predict) | Tempera-ture, °С
Calculation of 2009 | 25 dpa at the end of 2015 | 500-520
Current calculation | 30 dpa at the end of 2015 | 520-625

## Slide 11: Calculation of the Sh1 pin swelling
Swelling formula | Тirr, °С | Exposure dose D, dpa |  | 
 |  | 2015 | 2020 | 2025
 |  | D = 24.7 | D = 27.3 | D = 30.0
S0 = С ·D1.88 × × exp[–1.83·10– 4·(Tirr – 470)2], C = 5.6·10–3 | 520 | 1.4 | 1.8 | 2.1
 | 530 | 1.2 | 1.4 | 1.7
 | 570 | 0.4 | 0.4 | 0.5
Critical swelling value 2,1 % on the Sh1 pin will be obtain at the end of 2025.

## Slide 12: Conclusion
Constant С was specified in the swelling formula of Fe-18Cr-10Ni-Ti steel at temperatures above 480 °С; recommended to use the specified formula is at follows:
S0 = 0.56·10–2 · D1.88 exp[–1.83 · 10–4 (T – 470)2], %.
The correctness of specified formula was confirmed by a good fit of calculated and experimental results that makes the formula applicable.

## Slide 13: Conclusion
The calculation by the specified formula showed that the pins swelling is 2.1 % at temperatures above 520 °С.
From the viewpoint of this component, it allowed the extension of the BOR-60 lifetime till 2025.
Additional data will be obtained in future on swelling of Fe-18Cr-10Ni-Ti steel used for manufacturing IR-1 and IR-2 components to increase the statistical relevancy of swelling dose-temperature dependence at high temperatures.